## Slide 1: Structure of Large Steam Turbines
P M V Subbarao
Professor
Mechanical Engineering Department
More Rules for Development of Power Plant Turbines!!

## Slide 2: Structure of Modern Rankine Cycle Power Plant

## Slide 3: Super Critical Cycle of Nordjyl land NO.3 Unit in Denmark
T2=350.8C
p2=7.5MPa
h2=3005kJ/kg
s2=6.183 kJ/kg.K
T3=580C
p2=7.5MPa
h2=3598kJ/kg
s2=6.998 kJ/kg.K
T4=361.9C
p4=2.0MPa
h4=3163kJ/kg
s4=6.998 kJ/kg.K
T5=580C
p5=2.0MPa
h5=3645kJ/kg
s4=7.65 kJ/kg.K
T6’=19.7C
p6’=2.3kPa
h6’=2047kJ/kg
s6’=6.998 kJ/kg.K
x6’=80.01%
T7=19.7C
p7=2.3kPa
h7=82.8kJ/kg
s7=0.2927 kJ/kg.K
T6”=19.7C
p6”=2.3kPa
h6”=1808kJ/kg
s6”=6.183 kJ/kg.K
X6”=70.3%
T1=580C
p1=29.0MPa
h1=3389 kJ/kg
s1=6.183 kJ/kg.K

## Slide 4: Basic Idea to Raise Final Feed Water Temperature
Approximate increase in cycle efficiency due to addition of nth FWH

## Slide 5: Train of Shell & Tube HXs.

## Slide 6: Typical ~ 500 MW Designs

## Slide 7: Typical ~ 800 MW Designs

## Slide 8: ~ 1000 MW Designs

## Slide 9: Some Facts about Advanced Steam Turbines

## Slide 10: Increased Magnitudes of Forces

## Slide 11: Steam Volume Variation HP Range
Chart: 
| 27.5 | 15 | 10 | 8 | 6
 | 0.01215 | 0.01937 | 0.02656 | 0.03163 | 0.03961
Steam Path, Mpa
Specific volume, m3/kg

## Slide 12: Steam Volume Variation IP Range
Chart: 
| 5.5 | 5 | 4.5 | 4 | 3.5 | 3 | 2.5 | 2 | 1.5 | 1 | 0.5
 | 0.07136 | 0.07693 | 0.08359 | 0.09171 | 0.1018 | 0.1149 | 0.1325 | 0.1577 | 0.1972 | 0.2699 | 0.46
Steam Path, Mpa
Specific volume, m3/kg

## Slide 13: Steam Volume Variation LP Range
Chart: 
| 0.5 | 0.4 | 0.30000000000000032 | 0.2 | 0.1 | 0.05 | 2.5000000000000001E-2 | 1.0000000000000005E-2 | 5.0000000000000114E-3 | 4.0000000000000114E-3
 | 0.46 | 0.5457 | 0.6798 | 0.9259 | 1.653 | 3.05 | 5.65 | 12.84 | 23.98 | 29.34
Steam Path, Mpa
Specific volume, m3/kg

## Slide 14: Bleeding for FWHs : A win-win Idea

## Slide 16: Mechanical Arrangements of Steam Turbines
More solutions to Turbo-machinery Issues.
Tandem Reheat Steam Turbine
Cross Compound Steam Turbine

## Slide 17: Tandem Reheat Steam Turbine

## Slide 18: Tandem-compound four-flow steam turbine

## Slide 19: Cross Compound Reheat Steam Turbine

## Slide 20: Large-Capacity Steam Turbines Thermal Power Plant

## Slide 21: Variation of Flow along the Blade Height : from Hub to Tip
Validity/consequence of the Meridional Plane Analysis???
No Impact of Radial variation of Blade velocity???

## Slide 22: Radial Direction of an Axial Flow Turbo-Machines
The third direction in an axial flow machine is the radial direction.
The direction of Centrifugal forces!
Strong centrifugal forces are exerted on blades & fluid in radial direction.
The centrifugal force field distorts the flow velocity profiles considerably, if there is a possibility.
Fluid particles (if there is a possibility) will tend to get accelerated outwards blade tip rather than passing along cylindrical stream surfaces as classically assumed.

## Slide 23: Radial Direction of an Axial Flow Turbo-Machines
Possibility is very high in the stages with tall blades.
An approach known as the radial equilibrium method, is widely used for three-dimensional design calculations in an axial flow machine.

## Slide 24: Radial Variation of Velocity Triangles

## Slide 25: Flow Through Stator, Rotor and More

## Slide 26: Flow in Stator-Rotor Inter stage Gaps

## Slide 27: Radial Equilibrium Theory
This theory aims to achieve radial equilibrium od the working fluid before and after a rotor blade row.
Radial movement will disturb the loading on the moving blade passage.
More significant for large Axial Flow Machines.
The fluid parcels in the gaps before and after must remain in radial equilibrium.

## Slide 28: Radial Equilibrium Analysis of an infinitesimal Fluid Parcel Rotor-Stator Gap
The centrifugal force = (rrdrdq)w2r
V= rw
The centrifugal force is
The pressure force on the element

## Slide 29
If the two forces are the only ones acting (viscous and other effects neglected), the particle will move at constant radius if:
Radial Equilibrium Analysis

## Slide 30: Equilibrium Pressure Field for A Rotating Fluid
Fluid particles entering or leaving a rotor blade must adjust their pressure field as per the law of radial equilibrium.
The fluid must be subjected to a thermodynamic process to achieve this equilibrium.
However, total enthalpy of the fluid will remain constant as there is no work transfer in this process.
This thermodynamic process is defined as :
Isentropic constant total enthalpy pressure adjustment process.

## Slide 31: Isentropic Process to Reach Radial Equilibrium
The radial variation of whirl velocity should be according to above equation.
Total enthalpy is conserved during this process!!

## Slide 32: Conservation of Total Enthalpy Along Radial Direction
Stagnation enthalpy should conserve along radial direction, as there are not interactions with rotor at inlet or exit of rotor.

## Slide 33: ODE for the Radial Equilibrium of Fluid Parcels

## Slide 34: ODE Governing the Radial Equilibrium
Radial equilibrium demands that radial component of velocity must be zero.

## Slide 35: Condition for Radial Equilibrium of Fluid Parcels