## Slide 1: Analysis of Irreversible Flow through Turbines
P M V Subbarao
Professor
Mechanical Engineering Department
Control & Minimization of Entropy Generation in Turbine Stages.……

## Slide 2: Structure of Large High-Pressure Turbine
2a
4a
5a

## Slide 3: Structure of Large High-Pressure Turbine

## Slide 4: Isentropic vs Irreversible Adiabatic Flow Through Turbine : SSSF
h0
s
4s (Exit, iso)
Ideal work wiso = h0,in – h0,exit,iso
Actual work wact = h0,in – h0,exit,act
4a,Exit,actual
3 (in)
s
The Lost Work due to irreversible flow

## Slide 5: Stagewise Distribution of Entropy Generation
3
4s
4IIs
4IIIs
4Is
4Vs
4IVs
4Ia
4IIa
4IIIa
4IVa
4Va
4VIs
4VIa
h0
s
Control Stage
Stage 1
Stage 2
Stage 3
Stage 4
Stage 5

## Slide 6: Sequence of Energy Losses in a Turbine Stage
Steam
kinetic
Power
Nozzle Losses
Moving Blade
Losses
Stage Losses
Isentropic efficiency of
Nozzle
Blade Friction Factor
Steam
Thermal
Power
Blade
kinetic
Power
Gap Losses

## Slide 7: BREAKDOWN OF STAGE LOSSES - 1
The work done on the rotor blades is indicated by the change in tangential momentum.
The overall integrated value can be calculated from the velocity conditions for the mass passing through the rotor blades.
The energy given up by the gas is more than this!
The difference is due to
the friction on the blade profiles, and loss in blade wakes (profile loss);
the friction on the walls at root and tip, and other end effects (secondary loss);
the sudden enlargements in the fluid path, or wall cavities (annulus loss).

## Slide 8: BREAKDOWN OF STAGE LOSSES - 2
Not all the fluid passes through the rotor blades, because of leakage through
  diaphragm glands,
  balance holes, and
  over the rotor blade tips;
The actual work per unit total mass flow is less than the work done on the blades per unit blade mass flow as evaluated in the last slide.
Windage and bearing losses reduce the coupling power below that produced at the blades.
Losses resulting from partial admission lacing wire and wetness losses are also similar to windage loss.

## Slide 9: Classification of Losses based on Mutual Interaction
Group I
Guide profile loss.
Runner profile loss.
Guide secondary loss.
Runner secondary loss.
Guide annulus loss
Runner annulus loss
Group 2
Guide gland leakage loss.
Balance hole loss.
Rotor tip leakage loss.
Lacing wire loss.
Wetness loss
Disc windage loss.
Losses due to partial admission.

## Slide 10: Classification of Losses based on Mutual Interaction
Group I
Guide profile loss.
Runner profile loss.
Guide secondary loss.
Runner secondary loss.
Guide annulus loss
Runner annulus loss

## Slide 11: Classification of Losses based on Mutual Interaction
Group I
Guide profile loss.
Runner profile loss.
Guide secondary loss.
Runner secondary loss.
Guide annulus loss
Runner annulus loss

## Slide 12: Classification of Losses based on Mutual Interaction
Group I
Guide profile loss.
Runner profile loss.
Guide secondary loss.
Runner secondary loss.
Guide annulus loss
Runner annulus loss

## Slide 13: Classification of Losses based on Mutual Interaction
Group 2
Guide gland leakage loss.
Balance hole loss.
Rotor tip leakage loss.
Lacing wire loss.
Wetness loss
Disc windage loss.
Losses due to partial admission.

## Slide 14: Classification of Losses based on Mutual Interaction
Group 2
Guide gland leakage loss.
Balance hole loss.
Rotor tip leakage loss.
Lacing wire loss.

## Slide 15: Classification of Losses based on Mutual Interaction
Group 2
Guide gland leakage loss.
Balance hole loss.
Rotor tip leakage loss.
Lacing wire loss.
Wetness loss
Disc windage loss.
Losses due to partial admission.

## Slide 16: Classification of Losses based on Mutual Interaction
Group 2
Guide gland leakage loss.
Balance hole loss.
Rotor tip leakage loss.
Lacing wire loss.
Wetness loss
Disc windage loss.
Losses due to partial admission.

## Slide 17: Classification of Losses based on Mutual Interaction
Group 2
Guide gland leakage loss.
Balance hole loss.
Rotor tip leakage loss.
Lacing wire loss.
Wetness loss
Disc windage loss.
Losses due to partial admission.

## Slide 18: Classification of Losses based on Mutual Interaction
Group 2
Guide gland leakage loss.
Balance hole loss.
Rotor tip leakage loss.
Lacing wire loss.
Wetness loss
Disc windage loss.
Losses due to partial admission.

## Slide 19: Classification of Losses based on Mutual Interaction
Group 2
Guide gland leakage loss.
Balance hole loss.
Rotor tip leakage loss.
Lacing wire loss.
Wetness loss
Disc windage loss.
Losses due to partial admission.

## Slide 20: Blading Efficiency
A blading efficiency can be defined as
Referring to the mass flow passing through the rotor blade.

## Slide 21: The Overall Stage Efficiency
The overall stage efficiency is then defined in a similar form as
Referring to the mass flow passing through the stage.

## Slide 22: Physical Locations for Occurrence of Losses

## Slide 23: Physical Locations for Occurrence of Losses

## Slide 24: INFLUENCE PARAMETERS
The loss generation in a turbine stage are a function of many parameters:
Reynolds number Re and Mach number M
Aspect ratio, h/s.
Pitch–chord ratio, t/s.
Relative flow turning,
Ratio of relative velocities
Blade loading parameter
Inlet boundary layer
Boundary layer at the trailing edge
Leakage flow interaction.

## Slide 25: PROFILE LOSSES
Historically, one essential feature sought during 2D profile section design for a given velocity triangle has been to reach minimum loss.
This includes skin friction on the profile surface and trailing edge loss.
Owing to higher velocity levels and the occurrence of adverse pressure gradients, the skin friction loss on a typical subsonic profile is mainly determined by the flow behaviour on the suction side.
Typically more than 80 per cent of the skin friction loss occurs on the suction side.

## Slide 26: Distribution of Entropy Generation in a Stage
Stage inlet, i
Stage Exit, es
eIIs
eIIIs
eIs
eVs
eIVs
eIa
eIIa
eIIIa
eIVa
eVa
eVIs
eVIa
h0
s
Stator flow path
Stator-rotor gap
Rotor flow Path
Inter-stage gap
…..

## Slide 27: Definition of Isentropic/adiabatic Efficiency
Relative blade efficiency is calculated as:
Internal Relative Efficiency is calculated as:

## Slide 28: Typical Distribution of Major Losses A Stages

## Slide 29: General Distribution of Stagewise Losses

## Slide 30: Parson’s concept of multi-stage had produced an additional but marginal thermodynamic advantage.

## Slide 31: Diverging Nature of Isobars on h-s Diagram
Chart: 
| 6 | 6.2 | 6.4 | 6.6 | 6.8 | 7
 | 2809 | 2920 | 3038 | 3165 | 3303 | 3453
 | 3057 | 3200 | 3352 | 3516 | 3692 | 3882
h
s
High Pressure
Low Pressure

## Slide 32: Behavior of Superheated Steam at Constant Pressure
Chart: 
| 500 | 510 | 520 | 530 | 540 | 550 | 560 | 570 | 580 | 590 | 600
 | 3238 | 3271 | 3302 | 3333 | 3364 | 3393 | 3423 | 3452 | 3481 | 3509 | 3538
h
T

## Slide 33: Well Behavior of Superheated Steam
Chart: 
| 500 | 510 | 520 | 530 | 540 | 550 | 560 | 570 | 580 | 590 | 600
 | 3.1719 | 3.1279 | 3.0839 | 3.0399 | 2.9959 | 2.9519 | 2.9079 | 2.8639 | 2.8199 | 2.7759 | 2.7319
T

## Slide 34
Internal Reheating due to Irreversibilities
3
4s
4IIs
4IIIs
4Is
4Ia
4IIa
4IIIa
4Vs
4IVs
4IVa
4Va
4VIs
4VIa
h0
s

## Slide 35: Steam Flow Path in a Multi-Stage Impulse Turbine
Global available enthalpy for Power:
3
4s
4IIs
4IIIs
4Is
4Vs
4IVs
4Ia
4IIa
4IIIa
4IVa
4Va
4VIs
4VIa
Internally available enthalpy for Power:
Total actual stage work output per unit mass:
4IIss
4IIIss
4IVss
4Vss

## Slide 36
Define Stage Efficiency:
Global internal efficiency of turbine:
Improved Behavior of A Sequential Group of Stages

## Slide 37
qi is always positive.
Therefore,
Multistage turbines will increase the possibility of recovering lost work!
The larger the number of stages, the greater is the heat recovery.
The difference is called heat recovery factor, a.
General value of a is 0.04 to 0.06.
Reheat Factor

## Slide 38
Advanced 700 8C Pulverised Coal-fired Power Plant Project