## Slide 1: Two Phase Convection Heat Transfer & Cooling Systems for High Speed Electronic Devices
Unleashing Maximum Heat Transfer for Next-Gen Digital Industry….…..
P M V Subbarao
Professor
Mechanical Engineering Department
I I T Delhi

## Slide 2: Dielectric Fluids & Typical heat transfer coefficients
Convection Systems for Future

## Slide 3: Heat Flux Generated by High End Computing Processors

## Slide 4: Heat Flux Generated by High End Computing Processors
Training algorithms for artificially intelligent applications requires large amounts of processing powers.
Dense GPU processors are deployed for this applications.
A large number of high powered GPU produce high heat.
Two phase cooling is most cost efficient and eco-friendly cooling solution.

## Slide 5: Direct Cooling by Boiling Process : A Self Regulated Cooling Mechanism

## Slide 6: Direct Cooling by Boiling Process : A Self Regulated Cooling Mechanism
Boiling processes can be divided into;
  Pool boiling
  External flow boiling
  Hybrid configurations with their combinations
The Pool Boiling (PB) is the simplest scheme among the above-mentioned boiling configurations.
PB has significant benefit of so-called passive cooling without requiring pumping power or moving parts in the system.

## Slide 7: Two-phase Immersion Cooling Cycle of Gigabyte Servers

## Slide 8: Case Temperature vs Coolant Pressure
Liquid
Liquid
vapour
Liquid
SaturaredLiquid + Vapour
Internal Energy, kJ
Select fluid at a given pressure in a tank
Single phase cooling conditions:
Coolant can take a heat of mcT.
Ex: 1gm of water with 10 C raise in temperature can carry a heat of 42J.

## Slide 9: Case Temperature vs Coolant Pressure
Liquid
Liquid
vapour
Liquid
SaturaredLiquid + Vapour
Internal Energy, kJ
Two phase cooling may be possible.
Coolant can take a heat of mufg.
Ex: 1gm of water becoming steam can carry a heat of  2500J.
Boiling coolant can develop compact and efficient cooling systems.

## Slide 10: Basic Definitions for Boiling Heat Transfer Process
Liquid
Liquid
vapour
Liquid
SaturaredLiquid + Vapour
Internal Energy, kJ
Initial studies showed that heat flux (q”) plays an important role along wall superheat in boiling process.

## Slide 11: Boiling Curve &Modes of Boiling

## Slide 12: Two Phase Cooling Below Critical Heat Flux

## Slide 13: Heat Sinks to Maintain Safe Margin

## Slide 14: Nucleate Pool Boiling: Bubble Dynamics

## Slide 15: Bubble growth on CPU Direct-Cooling
The process of liquid nucleate boiling includes three basic heat transfer episodes:

## Slide 16: Episode 1: Immediately after Departure of Bubble
The departure of bubble from the CPU wall leads to occurrence of the unsteady heat transfer process between the liquid and the heating surface (CPU wall).
The lower temperature liquid enters the heating surface and the nearby space is occupied by the original bubble.
This new liquid will be in direct contact with the heating surface for a period of time.
 A heat flux q”re is required for reconstruction of the thermal boundary layer just after the bubble breaks away.
The duration of occurrence of this heat flux is named as the waiting time before the bubble starts to grow.

## Slide 17: Episode 2
This episode starts with initiation of bubble growth.
A thin layer of liquid at the bottom of the bubble absorbs heat from the heating surface and vaporizes when the bubble grows.
The evaporation heat flux q”me is provided to the growth of the vapor bubble through heat conduction of the liquid microlayer.
The growth time from the beginning of the bubble growth to when it leaves will have evaporation heat flux.

## Slide 18: Episode 3
The natural convection heat transfer process between the heating surface and the liquid is always present in a boing process.
The natural convective heat flux density q”nc of the area is not affected by the growth and separation of the bubble.
The growth and separation of the bubble on the heating surface cause disturbance to the nearby liquid, which greatly intensifies this process.
The overall heat flux density on the wall is given by the following Equation:

## Slide 19: Nucleate Pool Boiling: Bubble Diameter
The average diameter of bubble departing from hot surface of a processor is:

## Slide 20: Nucleate Pool Boiling: Minimum Wall Superheat
The minimum degree of superheat required to nucleate pool boiling depends on a non-dimensional number known as Jacob Number

## Slide 21: Models for Nucleate Pool Boiling
Jacob Number is function of Reynolds and Prandtl numbers
The value of s varies in the range 1 – 1.7.
CNBHT is to be determined for every case.

## Slide 22: Nucleate Pool Boiling: Minimum Wall Superheat

## Slide 23: Nucleate Pool Boiling : Selection of Pressure

## Slide 24: Correlations for Heat Transfer Coefficient
Considering its complexity, there is no widely accepted analytical equation for boiling heat transfer at present.
In order to meet the needs of engineering, many researchers use a large number of experimental data to obtain many boiling heat transfer equations.
Three boiling heat transfer equations have been considered as more useful here:
Shiraishi Correlation

## Slide 25: Correlations for Heat Transfer Coefficient
Cooper Correlation
Kutateladze Correlation

## Slide 26: Predicted & Measured Heat Transfer Coefficient

## Slide 27: Microchannel Lid Cold Plate（MLCP）
MLCP is a key technology for high-power chip cooling.
It integrates the traditional chip lid and liquid cold plate into a single component.
Facilitates the coolant to flow directly over the chip through micro-scale channels (30–150 microns).

## Slide 28: Flow Boiling Process
Flow boiling occurs when all the phases are in bulk flow together in a channel.
The flow boiling is characterized by the forced convective flow over a surface induced by the external force, e.g. a pump.

## Slide 29: CHF mechanisms for flow boiling in uniformly heated channel: Subcooled Liquid
T, C
Specific Enhalpy, h (kJ/kg)

## Slide 30: Micro-Channel versus Macro-Channel Flow Boiling
Pipe diameters of 100–600 m is classified as micro-channels.
Distinguishing between macro- and micro-channel flows cannot be based on channel size alone.
A channel may behave as a micro-channel for certain fluids and operating conditions and as a macro-channel for others.
For two-phase flow, this boundary is closely related to the ratio of bubble size to channel diameter,
The larger the ratio, the more likely that the flow will behave as a micro-channel flow.
This ratio is known as Confinement number.

## Slide 31: Micro-Channel Flow Boiling : Confinement Number
Confinement number, Co

## Slide 32: Classification of heat exchanger for different hydraulic diameters

## Slide 33: The microchannel Flow Boiling Device
Microchannel test section assembly contains a copper housing with inlet and outlet plenum, test chip and pressure transducers and thermocouples at inlet and outlet of the test chip..

## Slide 34: The microchannel Flow Boiling Device
Microchannel test chip:
Five parallel straight microchannels.
Each channel dimension is width, w: 220 μm × height, H: 250 μm × length, L: 10 mm. described in our previous study27.

## Slide 35: The microchannel Flow Boiling Device
The microchannel test chip is made from a silicon wafer bonded to a Pyrex wafer by a standard microfabrication process.

## Slide 36: The microchannel Flow Boiling Device
A resistor, which serves as both a micro heater to generate heat flux and a thermistor to measure the wall temperature, is deposited onto the back side of the silicon chip.

## Slide 37: The microchannel Flow Boiling Device
The heating area (length, L: 10 mm × width, W: 2 mm) is identical to the total base area of microchannel arrays.

## Slide 38: Fluid Dynamics of Flow Boiling

## Slide 39: Convection Heat Transfer in Flow Boiling

## Slide 40: Ullmann–Brauner Flow Regime Map

## Slide 41: Flow Pattern Transition in A microchannel Flow Boiling Device
To understand the flow pattern transition and flow regime development in flow boiling microchannels.
A series of high-speed visualization studies were employed from the top of microchannels.
Dielectric fluid HFE-7100 was adopted as the coolant.
Frame rate ranges between 4000 and 70,000 fps.
Mass flux, 400 kg/m2s and heat flux, 30 W/cm2.
First Step is to witness the flow Regimes.

## Slide 42: Flow Pattern Transition in A microchannel Flow Boiling Device

## Slide 43: Flow Pattern Transition in A microchannel Flow Boiling Device
Mass flux, 400 kg/m2s
Heat f lux, 30 W/cm2

## Slide 44: Flow Pattern Transition in A microchannel Flow Boiling Device

## Slide 45: Flow Boiling Maps

## Slide 46: Flow Boiling Maps

## Slide 47: Heat transfer coefficient Vs local vapor quality

## Slide 48: Micro-Channel Flow Boiling :Bond Number
Bond number is defined as the ratio of buoyancy force to surface tension force
B
Reynolds number, Re
Re

## Slide 49: Vapor confinement criteria

## Slide 50: Regime of Vapor confinement

## Slide 51: Stable Flow Boiling of Confined Flow

## Slide 52: Stable Nature of Confined Flow

## Slide 53: Classification of heat exchanger for different hydraulic diameters

## Slide 54: Correlation for CHF
CHF correlations are based on either inlet (upstream) channel conditions or outlet (local) conditions.
Pressure, mass velocity and diameter appear in both types of correlations.
However, the effect of inlet quality in inlet conditions correlations is expressed in terms of inlet enthalpy (or inlet subcooling or quality).
These correlations also account for quality variations along the channel through their dependence on channel length

## Slide 56: Surface Roughness for Enhanced Heat Transfer
G = 85kg/m², Dryness Fraction, xexit = 0.3

## Slide 57: Surface Roughness for Enhanced Heat Transfer
G = 85kg/m², Dryness Fraction, xexit = 0.5

## Slide 58: Surface Roughness for Enhanced Heat Transfer
G = 85kg/m², Dryness Fraction, xexit = 0.8

## Slide 59: Surface Wettability for Enhanced Heat Transfer